SCOPE OF WORK

AND

TECHNICAL SPECIFICATIONS

FOR

PUUKAPU PASTORAL LOTS

WATER SYSTEM OPERATION & MAINTENANCE SERVICES

PUUKAPU, SOUTH KOHALA

ISLAND OF HAWAII, HAWAII

IFB NO.: IFB- 12-HHL-003

PREPARED BY

AKINAKA & ASSOCIATES, LTD.

PREPARED FOR

STATE OF HAWAII

DEPARTMENT OF HAWAIIAN HOME LANDS

SCOPE OF SERVICES FOR THE PUUKAPU PASTORAL LOTS WATER SYSTEM OPERATION & MAINTENANCE SERVICES, IN PUUKAPU, SOUTH KOHALA, HAWAII

Background

The Puukapu Pastoral Lots (PPL) Water System is a “non-DWS standard” system which provides potable water service to the PPL’ designated 186 parcels.  Copies of the Water Master Plan, approved by the County of Hawaii Department of Water Supply (DWS), and the Operation & Maintenance (O&M) Manual for the PPL water system are available for reference from the State of Hawaii Department of Hawaiian Home Lands (DHHL).

The PPL water system is connected to the County DWS’ system via a 4-inch master meter at the western end.  The PPL water system has two booster pump facilities to deliver water to service storage tanks.  Pump Station No. 1 is equipped with conventional electrically powered motors and pumps.  Due to its remoteness to available electrical power, Pump Station No. 2 is equipped by a diesel powered pump and a solar powered pump.

The PPL water system is designed to provide each of the 186 parcels with the DWS standard 400 gallons-per-day (Average daily flow) for a standard single-family service via a 5/8-inch sub-meter that will be issued to each lessee by DHHL.

Each lessee will be responsible to provide a backflow preventer after the sub-meter.  Some parcels serviced by the PPL water system (identified in the Water Master Plan) require an “Elevation Agreement” as the water pressure delivered to the subject parcel is below the DWS standard 40 psi due to an elevation constraint of the service tank.  These parcels will require the lessee to install and maintain individual facilities to provide the water pressure they desire for their parcel.

Fire protection for the PPL is provided by “static” fire tanks that have been located during the design of the system and reviewed/approved by the County Fire Department for strategic location and accessibility.  Standpipes at each fire tank facility provides for connection to fire fighting vehicles.

Scope of Services

The Contractor shall design-build, operate and maintain the appropriate chlorination facilities required to assure that the Puukapu Pastoral Lots Water System is compliant with the requirements of the State of Hawaii, Department of Health - Safe Drinking Water Branch.  The chlorination facilities shall include improvements required to disinfect the potable water and sample residual chlorine.  Such facilities shall be capable of adjustments to function from initial start-up of the system to the planned ultimate build-out of the Puukapu Pastoral Lots (186 single family services).

Rules and regulations for the Puukapu Pastoral Lots Water System, such as, but not limited to, billing rates and structure, meter purchase and distribution, and chlorination, as they pertain to existing Administrative Rules or laws of the State of Hawaii, DHHL and other government agencies including but not limited to the Department of Health and the Public Utilities Commission, and the Hawaiian Homes Commission Act, are still being promulgated.

Consequently the Contractor shall provide consulting services, as part of this contract, by advising DHHL during the formulation of draft rules and regulations for the Puukapu Pastoral Lots Water System that DHHL can adopt which take into account the nature of the system; it being “non-DWS Standard”, unique requirements identified by DHHL; such as input from the community deemed appropriate for implementation, and attempts to maximize the economic efficiency of its O&M and compliance with applicable state and Federal laws.

The Contractor shall perform complete operation, maintenance and repair services including inspections and emergency calls for all pumps, reservoirs, distribution water lines, telemetry systems, equipment and other appurtenances included under the contract, in accordance with the manufacturer’s specifications and recommended time intervals.

If the manufacturer does not provide these Operating and Maintenance (O & M) specifications, the Contractor shall contact the Contract Administrator or its designated representative and provide recommendations regarding the maintenance and repair of the specific equipment or system. Such service shall include regularly scheduled operation and maintenance tasks and inspections and any repairs required for each listed herein.

The maintenance and repair tasks and inspection shall consist of the furnishing of all labor, equipment, parts, materials and tools necessary to perform a thorough servicing and complete repair of all integral parts, lubricating, adjusting, and touch up painting where needed to keep the units in, or return to, a continuous operating condition. Maintenance of the system shall also include all activities such as routine flushing and water leak repair to insure water quality. All services performed will be subject to inspection and approval by the Department of Hawaiian Home Lands (DHHL) prior to start of work.

The Contractor shall be responsible for all tools and labor needed to perform the operation and maintenance services.  DHHL will reimburse the Contractor for parts and supplies on a cost plus 10% basis. This is under normal operations and maintenance and includes all appurtenances. The Contractor shall submit invoice copies with reimbursement request. Reimbursement request will not be accepted without invoice copies.

The Contractor will not be responsible for the cost of repairs due to flagrant vandalism, fire, storm or related damages that can be attributed to causes beyond his control such as acts of God; acts of a public enemy; acts of the State and any other governmental body in its sovereign or contractual capacity as described under General Condition Section 13 item d.  However, the Contractor shall be responsible for such repairs at no cost to the State if the damages are caused by the Contractor’s failure to properly maintain and service the systems and equipment.

The Contractor shall be responsible to provide and maintain a communication system to notify their maintenance personnel in the event of an emergency at the pump stations.

The Contractor shall also be responsible for all extraordinary incidents above the normal operation and maintenance including emergency call-outs and equipment breakdowns. The Contractor shall provide the Contract Administrator or its designated representative with following:

1.	Cost estimates if repairs can be made with in-house labor and materials. The Contractor will submit cost estimates to the Contractor Administrator or its designated representative for approval prior to starting work. Labor charges will be based on the rates for the applicable time situations listed on a current Wage Rate Schedule Bulletin published by the Department of Labor and Industrial Relations.  The current Wage Rate Schedule Bulletin is included in this IFB under the section titled IFB NOTIFICATION AND INFORMATION.  The current wage rate bulletin will be updated in mid February and that new bulletin can be obtained at www.hawaii.gov/labor. All material and equipment required shall be on a cost plus 10% basis. The Contractor shall submit invoice copies with reimbursement request. Reimbursement request will not be accepted without invoice copies.

2. 	If the Contractor requires using sub-contractors, in addition to in-house labor, or is more economically feasible (reduce down-time of system or special equipment or personnel to repair) to utilize outside sub-contractors, the Contractor shall be responsible to obtain quotations from sub-contractors and submit to the Contract Administrator for review. Charges for work performed by the sub-contractor will be for only the dollar amount quoted. The Contractor shall submit invoice copies with reimbursement request. Reimbursement request will not be accepted without invoice copies.

Such services require the approval of the Contract Administrator or its designated representative prior to commencement of work.

All normal operations performed by the Contractor shall include, but not be limited to the following applicable listed items:

A.	FAMILIARIZATION OF WATER SYSTEM STARTUP: The purpose for this requirement is to insure that the Contractor is able to startup the system in the event of a power outage, equipment breakdown or heavy storms and flooding for which the Contractor shall be responsible and accountable.

The Contractor shall:

1.	Operate the entire water system. A DHHL representative shall be present 	for training purposes.

2.	Maintain a regular maintenance log for record keeping of essential

equipment needed to operate the system such as operating hours of pumps, water level indicators and alarm systems. Contractor shall submit format of logbook and determination of essential equipment based on the Department of Health (DOH) requirements and approval of DHHL.

3.	Identify and establish water sample points and frequency of sampling

throughout the entire water system for Coliform testing and Chlorine Residual system pursuant to the DOH requirements. Contractor shall be responsible for the submission of sample site plan to DOH and DHHL for approval.

- OPERATIONS AND MAINTENANCE OF THE WATER SYSTEM

- BACKFLOW PREVENTION ASSEMBLY

  - Annually

    - Inspect and test the backflow prevention assembly, installed after the Department of Water Supply (DWS) master meter.

    - Repair the backflow prevention assembly as required per manufacturer’s recommendations in accordance with DWS standards and typical industry practices, to assure that the backflow prevention assembly functions as intended to protect integrity of the DWS water system.

- PUMP SYSTEMS

  - Twice weekly

    - Inspect, adjust, repair and or replace if necessary, after receiving approval from DHHL, all pump systems, including the chlorine metering pump system.

    - Inspect, adjust, repair and or replace if necessary, after receiving approval from DHHL, flow metering and totalizer system.

    - Check, adjust and repair if necessary after receiving approval from DHHL, pumps for vibration, noise and proper operation.

  - Monthly

    - Check, adjust, repair and or replace if necessary, after receiving approval from DHHL, automatic pump control valves for proper operation.

    - Check seals on all pumps for leakage and adjust, repair and or replace as required.

    - Check for proper alignment of motor/pump coupling and adjust, repair and or replace if necessary after receiving approval from DHHL.

    - Check pump bearings for abnormal temperature and replace if necessary after receiving approval from DHHL.

    - Lubricate motor and pump bearings per manufacturer’s recommendations.

    - Check mounting bolts for tightness and tighten per manufacturer’s recommendations.

    - Clean motor starter contacts and replace if necessary.

    - Test, check and maintain the alarm system that notifies maintenance personnel of an emergency at the pump stations.

    - Clean solar array and conduct diagnostic testing of solar inverter per manufacturer’s recommendations.

  - Quarterly

    - Check and adjust automatic pump control system (tank to sequence switch assembly) for start/stop signal and repair if necessary after receiving approval from DHHL.

    - Check and adjust reservoir level indicator assembly for proper operation and level readings.

    - Inspect all sensors, gauges, monitors, control devices, and telemetry system and adjust through field calibration if necessary for proper operation.

  - Semi-Annually

    - Clean strainer.

    - Check all valves for proper operation, tightness and repair or replace if necessary after receiving approval from DHHL.

    - Thoroughly clean out all dust and dirt from inside of electrical panels and starters.

  - Annually

    - Scrape and sand bare metal and paint all rusted areas, pumps, solar array, and supporting struts for preventive maintenance.

    - Inspect condition of wiring and conduit from motor to starter and repair or replace if necessary, after receiving approval from DHHL.

    - Open, inspect, clean and test pressure regulating and automatic control valves for proper operation and pressure setting.

    - Inspect motor and submit report and recommendations to the DHHL in writing.

6.	Other

        - Investigate feasibility of replacing pump at Tank Site #1 with variable speed.

        - Pump including benefit/cost analysis and cost estimate.

        - Provide report of findings to DHHL for evaluation in pursuing funding for pump replacement if power costs (to DHHL) warrant such.

        - Include salvage, reuse, or sale or exchange of existing pump in the analysis.

- DISTRIBUTION SYSTEM

  - Twice weekly

    - Check chlorine residual at pump station sampling point(s); adjust chlorinator as needed to maintain required residual.

    - Ensure that there is sufficient supply of chlorine stock and coordinate replenishment of chlorine stock.

  - Monthly

    - Inspect, report and repair if necessary, after receiving approval from DHHL, surface areas above system pipelines for signs of roadway failure, soft spots, or leakage.

    - Check chlorine residual at distribution system dead ends.

    - Test and maintain Emergency-pumping equipment for proper operation.

  - Bi-Monthly

    - Inspect conditions of water meters and meter boxes, note signs of leakage, damage or tampering; repair or replace meter meters after receiving approval by DHHL.

    - Submit report of pump site log activities to the West Hawaii District Office, Department of Hawaiian Home Lands.

    - Inspect pressure-reducing station for proper operation; adjust as needed to maintain downstream pressure.

  - Semi-Annually

    - Check, exercise and adjust all valves for proper operation and tightness; repair or replace, if necessary, after receiving approval from DHHL.

    - Maintain integrity and cleanliness of Department of Health sampling stations.

    - Flush water mainlines as required or when contaminates are found, after repair of line breaks and after major components are replaced to insure that chlorination reaches dead end lines.

    - Flush inter-connection manifold system.

    - Utility poles for power or telemetry systems.  Notify DHHL if repairs or replacement are warranted.

  - Annually

    - Inspect and fire tanks, valves, and other exposed plumbing for preventive maintenance.

    - Inspect valve markers, for rust or deteriorated paint, and repaint per original color pattern as needed or if requested by DHHL.

- WATER STORAGE SYSTEM

  - Daily

    - Check tank and booster pump system for vandalism.

    - Report any vandalism to the appropriate jurisdictions.

    - Repair breaches or damages to perimeter fence within 24 hours.

  - Quarterly

    - Check storage system for the following, and repair if necessary, after receiving approval by DHHL:

          - Water storage tanks for leaks.

          - Damaged vent screens

          - Lock on entry port

          - Safety condition of ladder

          - Water level mechanism

          - Operating overflow check valve

          - Conditions of exterior tank surface coating.

    - Send quarterly reports to the West Hawaii District Office.

  - Tri-Annually

    - Inspect, repair and paint tanks and ladders as dictated by inspection or if requested by DHHL.

- GENERAL SITE MAINTENANCE

  - Cut brush and weeds, and remove all rubbish within fence line of booster pump and storage tank sites.

  - Cut and remove brush and weeds within fence of fire tank sites.

  - Apply herbicide to access road and tank perimeter road, and a 2-foot wide strip around the solar array at Tank Site #2, every four months.

  - Fire Tanks Only – inspect stand pipes and stand pipe bollards, for rust or deteriorated paint, and repaint per original color as needed or if requested by DHHL.

- LABORATORY TESTING AND REPORTING

  - The Contractor shall be responsible to obtain and deliver samples on a timely basis to a certified laboratory that is approved by the DOH. All cost including labor to obtain samples, cost to conduct the sample analysis, material cost such as the cost of sample containers and chill coolers, deliver/freight costs to ship samples to the respective laboratories including Phase V testing shall be the Contractor’s responsibility. Contractor to submit all documents pertaining to samples, results, and correspondence from the DOH to DHHL for review. All laboratory sampling shall comply with the Amended Safe Drinking Water Act and the State DOH regulations and requirements.

  - Monthly

    - Collect, preserve and transport bacteriological samples to the DOH laboratory in accordance with DOH Sampling guidelines and scheduling.

    - Act as liaison between DHHL and DOH regarding procedures, sanitary surveys, and other regulatory matters; meet with DOH personnel at site as requested to answer questions and/or disseminate information regarding operation of the system.

  - As required by DOH, the contractor shall collect, preserve and transport bacteriological samples to the DOH Laboratory in accordance with sampling guidelines and scheduling required for Phase Contaminants Testing.

  - Annually, the contractor shall:

    - Collect, preserve and transport water samples to the DOH laboratory in accordance with DOH lead and copper sampling guidelines and scheduling.

    - Collect, preserve and transport water samples to the DOH laboratory in accordance with DOH asbestos sampling guidelines and scheduling.

    - Evaluate results from DOH laboratory and submit summary reports to Safe Drinking Water Branch, with a copy to DHHL.

    - Comply with the Amended Safe Drinking Water Act describing quality of Puukapu Pastoral Lots Water System.

    - Write and make ready for distribution to consumers annually Water Consumer Confidence Report (CCR) as required by the DOH announced annual date.

  - Contamination Notification

In the event the water system indicates a contamination level above Safe Drinking Water Act and DOH requirements, it will be the responsibility of the Contractor to notify all service users and DHHL personnel accordingly and initiate corrective measures as required by the DOH.

- METERS AND BILLINGS

  - Bi-Monthly

    - Read all distribution system meters and calculate customer usage using handheld meter reading computer to be provided by the Contractor. Meters shall be read every two (2) months indicating the days of service provided which may vary from 59 to 61 days.

    - Forward copies of reports and water billing to DHHL West Hawaii District Office or other DHHL office as directed.

  - Purchase and install new meters in existing boxes and de-activate existing meters as authorized by DHHL representative. The Contractor shall submit invoice copies for reimbursement requests. Reimbursement request will not be accepted without invoice copies.  Clean and refurbish deactivated meters and store for reuse.  Return unused meters to DHHL at the end of the contract.

- CHLORINE AND OTHER SUPPLIES

Coordinate the ordering and receiving of chlorine and other supplies required for system operation such as gasoline for mowers, replacement parts for chlorine pump, electrical components and hoses. Replacement supplies will be the responsibility of the DEPARTMENT. The CONTRACTOR shall be reimbursed the cost of such items only with DHHL approval prior to purchase.

- EMERGENCY REPAIRS AND CALL-OUTS

Repair to equipment and appurtenances other than routine servicing described shall be performed as described under Scope of Services. Contractor shall respond to an emergency or a break in service within 60 minutes of notification.

- EMERGENCY RESPONSE PLAN

The Contractor shall prepare shall prepare and submit their Emergency Response Plan (ERP) to DHHL for review and approval.  The ERP shall have names and contact phone numbers of personnel responsible for the operation and maintenance of the Puukapu Pastoral Lots Water System.