SECTION 02718 – NON-POTABLE WATER SYSTEM

PART 1 – GENERAL

  - GENERAL CONDITIONS:  The General Conditions and Special Conditions preceding these specifications shall govern this section of the work.

  - WORK INCLUDED:  Furnish all labor, materials, tools, equipment and related items necessary to complete, in place, the potable water system in conformity with the dimensions, profiles, sections, and details shown on the plans.  Work shall be governed by the Water System Standards, Board of Water Supply, City and County of Honolulu, et al., State of Hawaii, 2002,” hereinafter referred to as the BWS Standards.

  - SUBMITTALS:

- Manufacturer’s certificates that pipe materials were sampled, tested and inspected, along with test results.

- Manufacturer’s installation instructions for PVC and ductile iron pipes and fittings.

PART 2 – PRODUCTS

  - MATERIALS:  All materials shall conform to the BWS Standards, unless herein specified.

- Non-potable water pipe shall be polyvinyl chloride (PVC), DR 18, conforming to AWWA C905.  Pipes shall be colored, Pantone 522 or equal.  The pipes shall be integrally stamped/marked “CAUTION:  RECYCLED WATER – DO NOT DRINK.”  The stamping/marking shall be on the top of the pipe.

- Purple identification tape, color index 77742 Violet #16, Pantone 512 or equal, shall be installed on top of concrete jackets longitudinally and shall be centered on the concrete jacket.  The identification tape shall be prepared with white or black printing on a purple field conforming to the above color, having words “CAUTION:  RECYCLED WATER – DO NOT DRINK.”  The width of the tape shall be at least three (3) inches in width.  The tape shall be continuous in its coverage on the jacket and shall be fastened to the jacket no more than ten (10) feet apart.

- Fittings:  Ductile iron fittings shall comply with AWWA C110, AWWA C111 and AWWA C115. Fittings shall be colored purple, color index 77742 Violet #16, Pantone 512 or equal.  Fitting interiors shall be lined with polyethylene complying with ASTM D1248.  Lining shall be 40 mils thick (nominal); 35 mils minimum.

- Ductile iron pipes shall be Class 52.  Ductile iron pipes shall be colored purple, color index 77742 Violet, Pantone 512 or equal.  Ductile iron pipes shall be lined with polyethylene complying with ASTM D1248.  Lining shall be 40 mils thick (nominal); 35 mils minimum.

All ductile iron pipes, valves and fittings shall be wrapped with two layers of 8 mils polyethylene wrap.  Polywrap shall be colored purple, color index 77742 Violet #16, Pantone 512 or equal.  Alternatively, instead of purple polywrap, purple identification tape can supplement polywrap provided it complies with requirements listed under PVC pipe.  Payment for the exterior polyethylene wrap shall be incidental to the price for ductile iron pipe and fittings.

- Frames and covers of manholes, valve boxes and meter boxes shall comply with the requirements of the BWS Standards, except all castings with the wording “WATER” shall be modified to read “RECYCLED WATER.”  The covers shall be provided with a 24-inch long galvanized steel coil chain, 3/16-inch with 12 links per foot, and welded to the frame and cover.

- Paint Schedule:  Unless otherwise specified, all new exposed and existing metal, masonry or concrete surfaces and all miscellaneous items shall be coated using the systems specified in the Approved Materials List in Section 402 of the BWS Standards or approved equal.

PART 3 – EXECUTION

  - INSTALLATION:  The installation, testing and acceptance of water lines shall be governed by the BWS Standards.

The Construction Manager shall be responsible for precisely laying out the various utility lines shown on the contract plans as provided elsewhere in these specifications.  The location shown on the contract plans of the various existing utility lines which the new lines are to cross over or under or connect to were determined on the basis of the best information available; however, no assurance can be provided that the actual locations will be precisely as shown on the contract plans.  The Contractor shall verify the actual locations of existing utility lines to be crossed or connected to.

In performing all work, the Contractor shall exercise due care and caution necessary to avoid any damage to and impairment in the use of any existing utility lines.  Any damage inflicted on existing lines resulting from the Contractor’s operations shall be immediately repaired and restored as directed by the Construction Manager at the Contractor’s expense.

Connections to or the lowering or relocation of existing mains shall be done by the Contractor in accordance with the BWS Standards.  The Contractor shall furnish all necessary pipe, fittings, appurtenances and other incidental materials.

Trenching, pipe cushion and backfilling for the water main shall be in accordance with the BWS Standards.

The Contractor shall coordinate the connection of the new water line with the Construction Manager.  The Contractor shall inform the Construction Manager a minimum of one week prior to the date of the actual connection.  The inverts shown on the plans are approximate only, and the Contractor shall adjust the slope of the new water line as necessary to construct a fully functional and acceptable system.  The Contractor shall ensure that all piping, fittings, materials, tools, equipment and incidentals are at the site and ready for connection.

  - Install non-potable water electronic markers as specified in Section 02609 – Electronic Markers for Potable and Non-Potable Water Systems.

  - IDENTIFICATION PAINTING:  All above approved items, interiors of vaults and boxes and accessible items shall be colored purple, color index 77742 Violet #16, Pantone 512 or equal, in accordance with Section 303.27 Painting, of the Water Standards.  Payment for painting will not be made directly but shall be a part of the unit price for the item of which it is a part.

END OF SECTION